## KL Terminal Blocks
Cross section (mm²)/ number of conductors simultaneously connectable to the terminal
KL | Type | In [A] | Torque [Nm] |  | 1.5 | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300
| 1x16* | 75 | 5 Nm (2,5-16 mm2) | Al Cu | - | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | -
|  | 76 |  |  | 3 | 3 | 3 | 2 | 1 | 1
| 1x50* | 160 | 5Nm (2,5-16mm²) | Al Cu | - | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | -
|  |  | 10Nm (25-50mm²) |  |  | 3 | 3 | 3 | 3 | 2 | 1 | 1** | 1
| 2x50* | 200 | 5Nm (2,5-16mm²) | Al Cu | - | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | -
|  | 320 | 10Nm (25-50mm²) |  |  | 3 | 3 | 3 | 3 | 2 | 1 | 1** | 1
| 1x95* | 200 | 12Nm (16-50mm²) | Al Cu | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | 1 | - | - | - | - | -
|  | 245 | 22Nm (70-95mm²) | [6 empty] | 3 | 2 | 2 | 1 | 1** | 1
| 2x95* | 400 | 12Nm (16-50mm²) | Al Cu | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | 1 | - | - | - | - | -
|  | 490 | 22Nm (70-95mm²) | [6 empty] | 3 | 2 | 2 | 1 | 1** | 1
| 1x150* | 250 320 | 12Nm (25-50mm²) | Al Cu | - | - | - | - | - | - | 1 3 | 1 3 | 1 2 | 1 1 | 1 1 | 1 1** | 1 1 | - | - | -
22Nm (70-95mm²)
38Nm (120-150mm²)
| 2x150* | 500 640 | 12Nm (25-50mm²) | Al Cu | - | - | - | - | - | - | 1 3 | 1 3 | 1 2 | 1 1 | 1 1 | 1 1** | 1 1 | - | - | -
22Nm (70-95mm²)
38Nm (120-150mm²)
| 1x240* | 315 | 25Nm (35-120mm²) | Al Cu | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | -
|  | 425 | 55Nm (150-240mm²) | [8 empty] | 3 | 3 | 2 | 1 | 1 | 1 | 1** | 1
| 2x240* | 630 | 25Nm (35-120mm²) | Al Cu | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | -
|  | 850 | 55Nm (150-240mm²) | [8 empty] | 3 | 3 | 2 | 1 | 1 | 1 | 1** | 1
| 1x300* | 400 | 45 Nm (95-120 mm2) | Al Cu | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | 1
|  | 520 | 75 Nm (150-300 mm2) | [11 empty] | 2 | 2 | 1 | 1 | 1 | 1
| 2x300* | 800 | 45 Nm (95-120 mm2) | Al Cu | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | 1
|  | 1040 | 75 Nm (150-300 mm2) | [11 empty] | 2 | 2 | 1 | 1 | 1 | 1
* N = Blue = only for one neutral conductor
* PE = Yellow/green = only for one protective conductor
** Biggest fine-strand conductors
Cu conductors may be solid, multi-strand or fine-strand conductors. With fine strand conductors use of cable end sleeve is recommended but not required.

## KKL Cable Connectors
Cross section (mm²)/ number of conductors simultaneously connectable to the terminal
KKL | Type | In [A] | Torque [Nm] |  | 1.5 | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300
| 1x16 | 63 | 2,2Nm (1,5-16mm²) | Al Cu | 1 | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | - | - | - | -
[5 empty] | 3 | 3 | 3 | 2 | 1** | 1
| 1x50 | 160 | 5Nm (2,5-16mm²) | Al Cu | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | -
|  |  | 10Nm (25-50mm²) |  |  | 3 | 3 | 3 | 3 | 2 | 1 | 1** | 1
| 1x50N | 125 | 5Nm (2,5-16mm²) | Al Cu | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | -
|  |  | 10Nm (25-50mm²) |  |  | 3 | 3 | 3 | 3 | 2 | 1 | 1** | 1
| 1x50M | 125 | 5Nm (2,5-16mm²) | Al Cu | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | -
|  |  | 10Nm (25-50mm²) |  |  | 3 | 3 | 3 | 3 | 2 | 1 | 1** | 1
| 1x50T.1 | 125 | 5Nm (2,5-16mm²) | Al Cu | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | -
|  |  | 10Nm (25-50mm²) |  |  | 3 | 3 | 3 | 3 | 2 | 1 | 1** | 1
| 1x50T.2 | 125 | 5Nm (2,5-16mm²) | Al Cu | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | -
|  |  | 10Nm (25-50mm²) |  |  | 3 | 3 | 3 | 3 | 2 | 1 | 1** | 1
| 1x50T.3 | 125 | 5Nm (2,5-16mm²) | Al Cu | - | - | - | - | - | 1 | 1 | 1 | 1 | - | - | - | - | - | - | -
|  |  | 10Nm (25-50mm²) |  |  | 3 | 3 | 3 | 3 | 2 | 1 | 1** | 1
| 2x50 | 200 | 5Nm (2,5-16mm²) | Al Cu | - | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | -
|  | 320 | 10Nm (25-50mm²) |  |  | 3 | 3 | 3 | 3 | 2 | 1 | 1** | 1
| 2x50M | 200 | 5Nm (2,5-10mm²) | Al Cu | - | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | - | - | - | - | - | - | -
|  | 320 | 10Nm (16-50mm²) |  |  | 3 | 3 | 3 | 3 | 2 | 1 | 1** | 1
| 1x95 | 200 | 12Nm (16-50mm²) | Al Cu | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | 1 | - | - | - | - | -
|  | 245 | 22Nm (70-95mm²) | [6 empty] | 3 | 2 | 2 | 1 | 1** | 1
| 1x95M | 200 | 12Nm (16-50mm²) | Al Cu | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | 1 | - | - | - | - | -
|  | 245 | 22Nm (70-95mm²) | [6 empty] | 3 | 2 | 2 | 1 | 1** | 1
| 2x95 | 400 | 12Nm (16-50mm²) | Al Cu | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | 1 | - | - | - | - | -
|  | 490 | 22Nm (70-95mm²) | [6 empty] | 3 | 2 | 2 | 1 | 1** | 1
| 1x120 | 200 | 12Nm (16-50mm²) | Al Cu | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | 1 | 1 | - | - | - | -
|  | 245 | 22Nm (70-120mm²) | [6 empty] | 3 | 2 | 2 | 1 | 1** | 1 | 1
| 1x120RS | 200 | 12Nm (16-50mm²) | Al Cu | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | 1 | 1 | - | - | - | -
|  | 245 | 22Nm (70-120mm²) | [6 empty] | 3 | 2 | 2 | 1 | 1** | 1 | 1
| 1x120RSY | 200 | 12Nm (16-50mm²) | Al Cu | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | 1 | 1 | - | - | - | -
|  | 245 | 22Nm (70-120mm²) | [6 empty] | 3 | 2 | 2 | 1 | 1** | 1 | 1
| 1x120T | 200 | 12Nm (16-50mm²) | Al Cu | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | 1 | 1 | - | - | - | -
|  | 245 | 22Nm (70-120mm²) | [6 empty] | 3 | 2 | 2 | 1 | 1** | 1 | 1
| 1x120T.1 | 200 | 12Nm (16-50mm²) | Al Cu | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | 1 | 1 | - | - | - | -
|  | 245 | 22Nm (70-120mm²) | [6 empty] | 3 | 2 | 2 | 1 | 1** | 1 | 1
| 1x120T.2 | 200 | 12Nm (16-50mm²) | Al Cu | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | 1 | 1 | - | - | - | -
|  | 245 | 22Nm (70-120mm²) | [6 empty] | 3 | 2 | 2 | 1 | 1** | 1 | 1
| 1x120T.3 | 200 | 12Nm (16-50mm²) | Al Cu | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | 1 | 1 | - | - | - | -
|  | 245 | 22Nm (70-120mm²) | [6 empty] | 3 | 2 | 2 | 1 | 1** | 1 | 1
| 1x120TM | 200 | 12Nm (16-50mm²) | Al Cu | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | 1 | 1 | - | - | - | -
|  | 245 | 22Nm (70-120mm²) | [6 empty] | 3 | 2 | 2 | 1 | 1** | 1 | 1
| 1x150 | 250 320 | 12Nm (25-50mm²) | Al Cu | - | - | - | - | - | - | 1 3 | 1 3 | 1 2 | 1 1 | 1 1 | 1 1** | 1 1 | - | - | -
22Nm (70-95mm²)
38Nm (120-150mm²)
| 2x150 | 500 640 | 12Nm (25-50mm²) | Al Cu | - | - | - | - | - | - | 1 3 | 1 3 | 1 2 | 1 1 | 1 1 | 1 1** | 1 1 | - | - | -
22Nm (70-95mm²)
38Nm (120-150mm²)
| 2x150VB | 500 640 | 12 Nm (25-50 mm²) | Al Cu | - | - | - | - | - | - | 1 3 | 1 3 | 1 2 | 1 1 | 1 1 | 1 1** | 1 1 | - | - | -
22 Nm (70-95 mm²)
38 Nm (120-150 mm²)
| 2x150VB | 500 640 | 12 Nm (25-50 mm²) | Al Cu | - | - | - | - | - | - | 1 3 | 1 3 | 1 2 | 1 1 | 1 1 | 1 1** | 1 1 | - | - | -
22 Nm (70-95 mm²)
38 Nm (120-150 mm²)
| 1x240 | 315 | 25Nm (35-120mm²) | Al Cu | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | -
|  | 425 | 55Nm (150-240mm²) | [8 empty] | 3 | 3 | 2 | 1 | 1 | 1 | 1** | 1
| 2x240 | 630 | 25Nm (35-120mm²) | Al Cu | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | -
|  | 850 | 55Nm (150-240mm²) | [8 empty] | 3 | 3 | 2 | 1 | 1 | 1 | 1** | 1
| 2x240VB | 630 | 25Nm (35-120mm²) | Al Cu | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | -
|  | 850 | 55Nm (150-240mm²) | [8 empty] | 3 | 3 | 2 | 1 | 1 | 1 | 1** | 1
| 2x240VM | 630 | 25Nm (35-120mm²) | Al Cu | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | -
|  | 850 | 55Nm (150-240mm²) | [8 empty] | 3 | 3 | 2 | 1 | 1 | 1 | 1** | 1
| 1x300 | 400 | 45 Nm (95-120 mm2) | Al Cu | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | 1
|  | 520 | 75 Nm (150-300 mm2) | [11 empty] | 2 | 2 | 1 | 1 | 1 | 1
| 2x300 | 800 | 45 Nm (95-120 mm2) | Al Cu | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | 1
|  | 1040 | 75 Nm (150-300 mm2) | [11 empty] | 2 | 2 | 1 | 1 | 1 | 1
| 2x300VB | 800 | 45 Nm (95-120 mm2) | Al Cu | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | 1
|  | 1040 | 75 Nm (150-300 mm2) | [11 empty] | 2 | 2 | 1 | 1 | 1 | 1
| 2x300VM | 800 | 45 Nm (95-120 mm2) | Al Cu | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | 1
|  | 1040 | 75 Nm (150-300 mm2) | [11 empty] | 2 | 2 | 1 | 1 | 1 | 1
** Biggest fine-strand conductors
Cu conductors may be solid, multi-strand or fine-strand conductors. With fine strand conductors use of cable end sleeve is recommended but not required.

## KLH Cable Connectors
Cross section (mm²)/ number of conductors simultaneously connectable to the terminal
KLH | Type | In [A] | Torque [Nm] |  | 1.5 | 2.5 | 4 | 6 | 10 | 16 | 25 | 35 | 50 | 70 | 95 | 120 | 150 | 185 | 240 | 300
| 2x150 | 455 | 44 Nm (50-150 mm2) | Al Cu | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | - | - | -
|  | 579 | [10 empty] | 2 | 1 | 1 | 1 | 1
| 2x240 | 631 | 75 Nm (95-240 mm2) | Al Cu | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1 | 1 | 1 | -
|  | 806 | [12 empty] | 2 | 2 | 1 | 1 | 1
| 2x300 | 810 | 75 Nm (185-300 mm2) | Al Cu | - | - | - | - | - | - | - | - | - | - | - | - | - | 1 | 1 | 1
|  | 1035 | [15 empty] | 1 | 1 | 1
Cu conductors may be solid, multi-strand or fine-strand conductors. With fine strand conductors use of cable end sleeve is recommended but not required.